## MUX
Magnitude |  | MUX_ABCDE | MUX_ADC | Scale Factor
PSU Voltages | SF1_A Voltage | 0 | 0 | 3
| SF1_B Voltage | 1 | 0 | 3
| SF2_A Voltage | 2 | 0 | 3
| SF2_B Voltage | 3 | 0 | 3
| SF3_A Voltage | 4 | 0 | 3
| SF3_B Voltage | 5 | 0 | 3
| SF4_A Voltage | 6 | 0 | 3
| SF4_B Voltage | 7 | 0 | 3
| SF5_A Voltage | 0 | 1 | 3
| SF5_B Voltage | 1 | 1 | 3
| SF6_A Voltage | 2 | 4 | -1.68
| SF6_B Voltage | 3 | 4 | -1.68
PSU Currents | SF1_A Current | 0 | 2 | 1.25
| SF1_B Current | 1 | 2 | 1.25
| SF2_A Current | 2 | 2 | 1.25
| SF2_B Current | 3 | 2 | 1.25
| SF3_A Current | 4 | 2 | 1.25
| SF3_B Current | 5 | 2 | 1.25
| SF4_A Current | 6 | 2 | 1.25
| SF4_B Current | 7 | 2 | 1.25
| SF5_A Current | 4 | 1 | 1.25
| SF5_B Current | 5 | 1 | 1.25
| SF6_A Current | 6 | 1 | -1.25
| SF6_B Current | 7 | 1 | -1.25
SnI Voltages | SUP_42V_UNREG | 0 | 3 | 5
| SUP_35V_UNREG | 1 | 3 | 3
| SUP_16V_UNREG | 2 | 3 | 1.68
| SUP_32V_REG | 3 | 3 | 3
| SUP_16V_REG | 4 | 3 | 3
| SUP_12V_F_A | 5 | 3 | 3,68/3
| SUP_12V_F_B | 6 | 3 | 3,68/3
| SUP_12V_F_C | 7 | 3 | 3,68/3
| SUP_12V_F_D | - | 5 | 3,68/3
| SUP_n16_REG | 0 | 4 | -1.68
| SUP_n20_UNREG | 1 | 4 | -2
| INT_VCC_3V3 | 2 | 1 | 1
| INT_VCC_12V | 3 | 1 | 1
| INT_VCC_n12V | 4 | 4 | -1

## Typedefs
Category | Variable Type | Variable Name | Description | Used by Package | PSU/ SnI
General Status | BOOL | psuStatus | PSU connected and functioning (T) or disconnected and with minimum voltage (F) | SwitchOnCTRL | PSU
| BOOL | relayStatus | PSU's Relay connected (T) or disconnected (F) | RelayLibrary | PSU
| float | progValue | Programmed value for a PSU's RDAC when psuStatus=ON | VoltCurrCTRL | PSU
| BOOL | sniStatus | SnI defined as always connected and functioning (T) | - | SnI
| float | nominalVoltage | Theoretical voltage value for the voltage source. Detailed list in MUX HW Module. | - | SnI
Addressing | BYTE | bridgeI2CAdr | I2C Address of the I2CtoSPIBridge implemented in the PSU's Functional SlotCard (same for each two PSUs). | I2C&SPILibrary | PSU
| BYTE | rdacAdr | SPI Address of the PSU's RDAC. | I2C&SPILibrary | PSU
Alarm Arrays | float[4] | alarmLimitValues | If measured value exceeds/doesn't reach these values, the alarm task will trigger an alarm | AlarmCTRL | PSU/ SnI
| float[4] | alarmLimitTimes | number of measures that have to exceed/not reach the limit values in order to trigger an alarm | AlarmCTRL | PSU/ SnI
| BOOL[12] | alarmProtocols | Activate or ignore an alarm protocol (Shutdown, modify voltage, send message) when an alarm is triggered | AlarmCTRL | PSU/ SnI
| WORD[4] | alarmProtocolShutdown | PSUs to be switched off when alarm protocol shutdown is executed | AlarmCTRL | PSU/ SnI
| float[4] | alarmProtocolVoltage | New voltage value to be programmed when alarm protocl modify voltage is executed | AlarmCTRL | PSU
| int[4] | alarmCounters | AUXILIARY. Used by alarmTask to count the number of times a measure has exceeded/not reached the limit values | AlarmCTRL | PSU/ SnI
| BOOL[4] | alarmStatus | AUXILIARY. Set ON when alarmCounters reach the limit times, triggering the protocols. | AlarmCTRL | PSU/ SnI
| BOOL[4] | alarmLimitReached | AUXILIARY. Last received measure exceeds/doesn't reach the limit value | AlarmCTRL | PSU/ SnI
| BOOL[4] | alarmWatch | Alarm surveillance connected (Auxiliary values are updated and alarms can be triggered) or disconnected (Auxiliary values are left to "0"). | AlarmCTRL | PSU/ SnI
Resistors | int | rShunt | Internal Resistor value (see Functional Slotcards) used to generate a voltage value. | - | PSU
ADC | float | vOut | measured Voltage obtained from monitorTask | MonitorCTRL | PSU/ SnI
| float | cOut | measured Voltage obtained from alarmTask | MonitorCTRL | PSU
Initialization | int | initializationTimer | x100ms initial count for PSU switching-on | SwitchOnCTRL | PSU
| BOOL | ReadyToConnect | AUXILIARY. (T) when the initializationTimer has been reached and the PSU can be connected | SwitchOnCTRL | PSU
FLASH | DWORD | VerifyKey | AUXILIARY. Used for data verification | FlashMemCTRL | PSU/ SnI

## Errors
Description | Solution
“ERROR 2: Create File” in the MTTTY | Check the selected port (COM5 normally used) and the USB are the same. If problem persists, disconnect and reconnect the Controller slotcard.
TRAP in UI | Exception in the code. Printf method may be causing the error. Avoid use of this command
Printf trap | Use ftos to convert float numbers to strings and use iprintf with %s instead
OSTask with PIT0 doesnt work | The PTI0 is being used as timer for an interruption, but its required for OSDelay functions. Use PIT1.
RDAc values don't change but SPI and I2C busses are working | RDAC Control Register must be configured to allow value updates before reading. If problem persists, lower the SPI frequency. (<100KHz)
Output voltages change but the RDAC doesn't answer properly | Before receiving an answer in the SPI bus, the other RDAC (in the same SF) must be set to hig impedance

## Glosario
Abbreviation | Stands for
AC | alarmCounter (when referred to variable)
ALR | alarmLimitReached
ALT | alarmLimitTimes
AS | alarmStatus
AW | alarmWatch
AC | Alternate current (when referred to voltage)
A2D or ADC | Analog to digital Module in the Coldfire 5213
AGC | Automatic Gain Control
BNC | Bayonet Neill–Concelman connector
SSR | departamento de Señales, Sistemas y Radiocomunicaciones
ETSIT | Escuela Técnica Superior de Ingenieros de Telecomunicacion
GPIO | General Purpose Input Output pin
HW | Hardware
I2CtoSPIBridge | I2C bus to SPI bus Converter. Model
MCF5213 | Microcontroller Coldfire model 5213
ms | milliseconds
MUX | Multiplexer
MTTTY | Multi-Threaded Text Terminal using a Serial Communication
MoSCoW | Must, Should, Could, Won't
O.A. | Operational Amplifier
PSU | Power Supply Unit
PCB | Printed Circuit Board
RDAC | Rheostat Digital to Analog Converter. Model AD5292 from Amidata
COMx | serial COMmunication with number x
SF | Slotcard Functional
SW | Software
SnI | Supply and Inernal voltages
SR | System Requirement
TC | Test Case
TFG | Trabajo Fin de Grado
UML | Unified modeling language
UPM | Universidad Politécnica de Madrid
UI | User Interface
UR | User Requirement
DC | Direct Current

## Glosario adaptado
Abbreviation | Stands for
A2D or ADC | Analog to digital Module in the Coldfire 5213
AC | alarmCounter (variable)
AC | Alternate current (voltage)
AGC | Automatic Gain Control
ALR | alarmLimitReached
ALT | alarmLimitTimes
AS | alarmStatus
AW | alarmWatch
BNC | Bayonet Neill–Concelman connector
COMx | serial COMmunication with number x
DC | Direct Current
ETSIT | Escuela Técnica Superior de Ingenieros de Telecomunicacion
GPIO | General Purpose Input Output pin
HW | Hardware
I2CtoSPIBridge | I2C bus to SPI bus Converter. Model
MCF5213 | Microcontroller Coldfire model 5213
MoSCoW | Must, Should, Could, Won't
ms | milliseconds
MTTTY | Multi-Threaded Text Terminal using a Serial Communication
MUX | Multiplexer
O.A. | Operational Amplifier
PCB | Printed Circuit Board
PSU | Power Supply Unit
RDAC | Rheostat Digital to Analog Converter. Model AD5292 from Amidata
SF | Slotcard Functional
SnI | Supply and Inernal voltages
SR | System Requirement
SSR | departamento de Señales, Sistemas y Radiocomunicaciones
SW | Software
TC | Test Case
TFG | Trabajo Fin de Grado
UI | User Interface
UML | Unified modeling language
UPM | Universidad Politécnica de Madrid
UR | User Requirement